## CIRCUIT 1
DELDOT | [11 empty] | Below, Input the distance to each load | [8 empty] | Below, Input the load from the luminaire or junction for each phase
| Job: |  | Project No. |  |  |  | Sheet: | 1 | of x
Description: |  | Voltage Drop |  |  |  | Calc. by: | XXX | Date: | 2019-03-25 12:51 |  |  |  | FROM | TO | DISTANCE (FT) | [8 empty] | NAME | PHASE A | PHASE B
Circuit: | [5 empty] | Checked by: |  | Date: |  |  |  |  | LCC | JW | 765 | [7 empty] | Load 1: | JW | 2.26 | 4.52
[13 empty] | JW | L120 | 115 | [7 empty] | Load 2: | L120 | 2.26
VOLTAGE DROP CALCULATION | [12 empty] | L120 | L119 | 160 |  | Select the voltage of the system | [5 empty] | Load 3: | L119 |  | 2.26
[13 empty] | L119 | L108 | 250 | [7 empty] | Load 4: | L108 | 2.26
[13 empty] | L108 | L107 | 350 | [7 empty] | Load 5: | L107 |  | 2.26
|  | Voltage: | 120 | Total Amp-Ft of Worst Case: |  |  |  |  | 18475.5 |  |  |  | L107 | L106 | 270 | [7 empty] | Load 6: | L106 | 2.26
[13 empty] | L106 | L102 | 265 |  | Voltage: |  | 120 |  |  |  | Load 7: | L102 |  | 2.26
| Voltage Drop (V): |  | 3.9507 |  | Minimum Wire Size: |  |  |  | #2 |  |  |  | L102 | L101 | 260 | [7 empty] | Load 8: | L101 | 2.26
Load 9:
| Voltage Drop (%): |  | 3.292% | [19 empty] | Load 10:
Load 11:
| Percentage of Maximum Allowed Voltage Drop : | [7 empty] | 65.84% | [13 empty] | Load 12:
Load 13:
Load 14:
Load 15:
TO USE CALCULATOR, INPUT DATA IN CELLS HIGHLIGHTED IN YELLOW. DATA UNDER SECTIONS HIGHLIGHTED IN PINK WILL AUTO-POPULATE. THEN SEE RESULTS IN THE RESULTS TO THE LEFT.
NOTE: ALL CALCULATIONS ARE MADE ASSUMING A MAX ALLOWABLE VOLTAGE DROP OF 5% AND USING ABOVE WIRE SIZE. ALL CALCULATIONS INCLUDE A 10% FACTOR TO ACCOUNT FOR DISCREPENCIES IN MEASUREMENTS OF THE CIRCUIT LENGTH
CONDUIT FILL CALCULATION
NOTE: CONDUIT FILLS ARE CALCULATED ASSUMING ONE CIRCUIT OF THE MINIMUM WIRE SIZE IN THE CONDUIT
| RGS: | % FILL |  | PVC Sched. 80: |  | % FILL | PVC Sched. 40: |  | % FILL
| 2" | 20.54% |  | 2" |  | 24.36% | 2" |  | 21.27%
| 2.5" | 14.39% |  | 2.5" |  | 16.99% | 2.5" |  | 14.91% | [7 empty] | See Calculations Below
| 3" | 9.335% |  | 3" |  | 10.87% | 3" |  | 9.631%
| 3.5" | 6.993% |  | 3.5" |  | 8.057% | 3.5" |  | 7.189%
| 4" | 5.434% |  | 4" |  | 6.218% | 4" |  | 5.576%
Max of 26% fill for new conduits
[14 empty] | Effect on total loads |  |  | Total Loads |  |  | Positive = ^ | Neg = v | [5 empty] | Area of Typical Wire Sizes |  |  |  |  | Area of Schedule 80 PVC Conduit (In2) |  |  |  | Area of Schedule 40 PVC Conduit (In2)
[10 empty] | From | To | Distance (ft) |  | Phase A | Phase B |  | A | N | B |  |  | IF Luminaire is on Phase A, Amperage is positive | [5 empty] | Circ. Mils | In2 |  |  |  | 100% | 26% | FILL |  | 100% | 26% | FILL
[10 empty] | LCC | JW | 765 |  | 2.26 | -4.52 |  | 11.3 | 0 | -11.3 |  |  | If Luminaire is on Phase B, Amperage is negative |  |  |  |  | 4/0 | 211600 | 0.4754 |  |  | 2" | 2.874 | 0.74724 | 24.36% | 2" | 3.291 | 0.85566 | 21.27%
[10 empty] | JW | L120 | 115 |  | 2.26 | 0 |  | 9.04 | -2.26 | -6.78 |  |  | If no luminaire appears on a phase, Amperage is 0 |  |  |  |  | 3/0 | 167800 | 0.4072 |  |  | 2.5" | 4.119 | 1.0709 | 16.99% | 2.5" | 4.695 | 1.2207 | 14.91%
[10 empty] | L120 | L119 | 160 |  | 0 | -2.26 |  | 6.78 | 0 | -6.78 | [7 empty] | 2/0 | 133100 | 0.6505 |  |  | 3" | 6.442 | 1.6749 | 10.87% | 3" | 7.268 | 1.8897 | 9.631%
[10 empty] | L119 | L108 | 250 |  | 2.26 | 0 |  | 6.78 | -2.26 | -4.52 | [7 empty] | 1/0 | 105600 | 0.3039 |  |  | 3.5" | 8.688 | 2.2589 | 8.057% | 3.5" | 9.737 | 2.5316 | 7.189%
[10 empty] | L108 | L107 | 350 |  | 0 | -2.26 |  | 4.52 | 0 | -4.52 | [7 empty] | #1 | 83690 | 0.266 |  |  | 4" | 11.258 | 2.9271 | 6.218% | 4" | 12.554 | 3.264 | 5.576%
[10 empty] | L107 | L106 | 270 |  | 2.26 | 0 |  | 4.52 | -2.26 | -2.26 | [7 empty] | #2 | 66360 | 0.175
[10 empty] | L106 | L102 | 265 |  | 0 | -2.26 |  | 2.26 | 0 | -2.26 | [7 empty] | #4 | 41740 | 0.1333 |  |  | Area of RGS Conduit (In2)
[10 empty] | L102 | L101 | 260 |  | 2.26 | 0 |  | 2.26 | -2.26 | 0 | [7 empty] | #6 | 26240 | 0.1041 |  |  |  | 100% | 26% | FILL
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | #8 | 16510 | 0.0835 |  |  | 2" | 3.408 | 0.88608 | 20.54%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | [12 empty] | 2.5" | 4.866 | 1.2652 | 14.39%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | [12 empty] | 3" | 7.499 | 1.9497 | 9.335%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | [12 empty] | 3.5" | 10.01 | 2.6026 | 6.993%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | [12 empty] | 4" | 12.882 | 3.3493 | 5.434%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[11 empty] | Ampere Ft Calc |  |  |  |  | Wire Size Calculations |  |  |  | Voltage Drop Calculations
[11 empty] | A-N |  | B-N |  |  | Total Ampere Ft. |  | 18475.5 |  | Area of wire required(cm): |  |  | 43694.5575 |  | Max allowed voltage drop (V): |  |  | 6
[11 empty] | 8644.5 |  | 8644.5
[11 empty] | 1299.5 |  | 519.8 |  |  | Resistivity Constant: |  | 12.9 |  | Minimum necessary wire size: |  |  | #2 |  | Voltage drop using min wire size (V): |  |  | 3.9507 |  | Voltage Drop in %: | 3.292%
[11 empty] | 1084.8 |  | 1084.8
[11 empty] | 2260 |  | 565 |  | Maximum allowed voltage drop: |  |  | 5% |  |  |  |  | % of Max allowed Voltage drop using min wire size: |  |  |  |  | 65.84%
[11 empty] | 1582 |  | 1582
[11 empty] | 1830.6 |  | 0 |  |  | Voltage (V): |  | 120
[11 empty] | 598.9 |  | 598.9
[11 empty] | 1175.2 |  | 0 |  |  | Error Contingency: |  | 10%
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | ========= |  | ===========
[10 empty] | TOTAL: | 18475.5 | TOTAL: | 12995

## CIRCUIT 2
DELDOT | [11 empty] | Below, Input the distance to each load | [8 empty] | Below, Input the load from the luminaire or junction for each phase
| Job: |  | Project No. |  |  |  | Sheet: | 1 | of x
Description: |  | Voltage Drop |  |  |  | Calc. by: | XXX | Date: | 2019-03-25 12:51 |  |  |  | FROM | TO | DISTANCE (FT) | [8 empty] | NAME | PHASE A | PHASE B
Circuit: | [5 empty] | Checked by: |  | Date: |  |  |  |  | LCC | L1 | 90 | [7 empty] | Load 1: | L1 | 2.7
[13 empty] | L1 | L2 | 240 | [7 empty] | Load 2: | L2 |  | 2.7
VOLTAGE DROP CALCULATION | [12 empty] | L2 | L3 | 140 |  | Select the voltage of the system | [5 empty] | Load 3: | L3 | 2.7
[13 empty] | L3 | L4 | 100 | [7 empty] | Load 4: | L4 |  | 1.7
[13 empty] | L4 | L5 | 170 | [7 empty] | Load 5: | L5 | 1.7
|  | Voltage: | 120 | Total Amp-Ft of Worst Case: |  |  |  |  | 18657.5 |  |  |  | L5 | L6 | 160 | [7 empty] | Load 6: | L6 |  | 1.7
[13 empty] | L6 | L7 | 105 |  | Voltage: |  | 120 |  |  |  | Load 7: | L7 | 2.7
| Voltage Drop (V): |  | 3.9896 |  | Minimum Wire Size: |  |  |  | #2 |  |  |  | L7 | L8 | 210 | [7 empty] | Load 8: | L8 |  | 2.7
[13 empty] | L8 | L9 | 200 | [7 empty] | Load 9: | L9 | 2.7
| Voltage Drop (%): |  | 3.325% | [9 empty] | L9 | L10 | 200 | [7 empty] | Load 10: | L10 |  | 2.7
[13 empty] | L10 | L11 | 190 | [7 empty] | Load 11: | L11 | 2.7
| Percentage of Maximum Allowed Voltage Drop : | [7 empty] | 66.49% |  |  |  | L11 | L12 | 190 | [7 empty] | Load 12: | L12 |  | 2.7
Load 13:
Load 14:
Load 15:
TO USE CALCULATOR, INPUT DATA IN CELLS HIGHLIGHTED IN YELLOW. DATA UNDER SECTIONS HIGHLIGHTED IN PINK WILL AUTO-POPULATE. THEN SEE RESULTS IN THE RESULTS TO THE LEFT.
NOTE: ALL CALCULATIONS ARE MADE ASSUMING A MAX ALLOWABLE VOLTAGE DROP OF 5% AND USING ABOVE WIRE SIZE. ALL CALCULATIONS INCLUDE A 10% FACTOR TO ACCOUNT FOR DISCREPENCIES IN MEASUREMENTS OF THE CIRCUIT LENGTH
CONDUIT FILL CALCULATION
NOTE: CONDUIT FILLS ARE CALCULATED ASSUMING ONE CIRCUIT OF THE MINIMUM WIRE SIZE IN THE CONDUIT
| RGS: | % FILL |  | PVC Sched. 80: |  | % FILL | PVC Sched. 40: |  | % FILL
| 2" | 20.54% |  | 2" |  | 24.36% | 2" |  | 21.27%
| 2.5" | 14.39% |  | 2.5" |  | 16.99% | 2.5" |  | 14.91% | [7 empty] | See Calculations Below
| 3" | 9.335% |  | 3" |  | 10.87% | 3" |  | 9.631%
| 3.5" | 6.993% |  | 3.5" |  | 8.057% | 3.5" |  | 7.189%
| 4" | 5.434% |  | 4" |  | 6.218% | 4" |  | 5.576%
Max of 26% fill for new conduits
[14 empty] | Effect on total loads |  |  | Total Loads |  |  | Positive = ^ | Neg = v | [5 empty] | Area of Typical Wire Sizes |  |  |  |  | Area of Schedule 80 PVC Conduit (In2) |  |  |  | Area of Schedule 40 PVC Conduit (In2)
[10 empty] | From | To | Distance (ft) |  | Phase A | Phase B |  | A | N | B |  |  | IF Luminaire is on Phase A, Amperage is positive | [5 empty] | Circ. Mils | In2 |  |  |  | 100% | 26% | FILL |  | 100% | 26% | FILL
[10 empty] | LCC | L1 | 90 |  | 2.7 | 0 |  | 15.2 | -1 | -14.2 |  |  | If Luminaire is on Phase B, Amperage is negative |  |  |  |  | 4/0 | 211600 | 0.4754 |  |  | 2" | 2.874 | 0.74724 | 24.36% | 2" | 3.291 | 0.85566 | 21.27%
[10 empty] | L1 | L2 | 240 |  | 0 | -2.7 |  | 12.5 | 1.7 | -14.2 |  |  | If no luminaire appears on a phase, Amperage is 0 |  |  |  |  | 3/0 | 167800 | 0.4072 |  |  | 2.5" | 4.119 | 1.0709 | 16.99% | 2.5" | 4.695 | 1.2207 | 14.91%
[10 empty] | L2 | L3 | 140 |  | 2.7 | 0 |  | 12.5 | -1 | -11.5 | [7 empty] | 2/0 | 133100 | 0.6505 |  |  | 3" | 6.442 | 1.6749 | 10.87% | 3" | 7.268 | 1.8897 | 9.631%
[10 empty] | L3 | L4 | 100 |  | 0 | -1.7 |  | 9.8 | 1.7 | -11.5 | [7 empty] | 1/0 | 105600 | 0.3039 |  |  | 3.5" | 8.688 | 2.2589 | 8.057% | 3.5" | 9.737 | 2.5316 | 7.189%
[10 empty] | L4 | L5 | 170 |  | 1.7 | 0 |  | 9.8 | 0 | -9.8 | [7 empty] | #1 | 83690 | 0.266 |  |  | 4" | 11.258 | 2.9271 | 6.218% | 4" | 12.554 | 3.264 | 5.576%
[10 empty] | L5 | L6 | 160 |  | 0 | -1.7 |  | 8.1 | 1.7 | -9.8 | [7 empty] | #2 | 66360 | 0.175
[10 empty] | L6 | L7 | 105 |  | 2.7 | 0 |  | 8.1 | 0 | -8.1 | [7 empty] | #4 | 41740 | 0.1333 |  |  | Area of RGS Conduit (In2)
[10 empty] | L7 | L8 | 210 |  | 0 | -2.7 |  | 5.4 | 2.7 | -8.1 | [7 empty] | #6 | 26240 | 0.1041 |  |  |  | 100% | 26% | FILL
[10 empty] | L8 | L9 | 200 |  | 2.7 | 0 |  | 5.4 | 0 | -5.4 | [7 empty] | #8 | 16510 | 0.0835 |  |  | 2" | 3.408 | 0.88608 | 20.54%
[10 empty] | L9 | L10 | 200 |  | 0 | -2.7 |  | 2.7 | 2.7 | -5.4 | [12 empty] | 2.5" | 4.866 | 1.2652 | 14.39%
[10 empty] | L10 | L11 | 190 |  | 2.7 | 0 |  | 2.7 | 0 | -2.7 | [12 empty] | 3" | 7.499 | 1.9497 | 9.335%
[10 empty] | L11 | L12 | 190 |  | 0 | -2.7 |  | 0 | 2.7 | -2.7 | [12 empty] | 3.5" | 10.01 | 2.6026 | 6.993%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | [12 empty] | 4" | 12.882 | 3.3493 | 5.434%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[11 empty] | Ampere Ft Calc |  |  |  |  | Wire Size Calculations |  |  |  | Voltage Drop Calculations
[11 empty] | A-N |  | B-N |  |  | Total Ampere Ft. |  | 18657.5 |  | Area of wire required(cm): |  |  | 44124.9875 |  | Max allowed voltage drop (V): |  |  | 6
[11 empty] | 1458 |  | 1188
[11 empty] | 2592 |  | 3816 |  |  | Resistivity Constant: |  | 12.9 |  | Minimum necessary wire size: |  |  | #2 |  | Voltage drop using min wire size (V): |  |  | 3.9896 |  | Voltage Drop in %: | 3.325%
[11 empty] | 1890 |  | 1470
[11 empty] | 810 |  | 1320 |  | Maximum allowed voltage drop: |  |  | 5% |  |  |  |  | % of Max allowed Voltage drop using min wire size: |  |  |  |  | 66.49%
[11 empty] | 1666 |  | 1666
[11 empty] | 1024 |  | 1840 |  |  | Voltage (V): |  | 120
[11 empty] | 850.5 |  | 850.5
[11 empty] | 567 |  | 2268 |  |  | Error Contingency: |  | 10%
[11 empty] | 1080 |  | 1080
[11 empty] | 0 |  | 1620
[11 empty] | 513 |  | 513
[11 empty] | 0 |  | 1026
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | ========= |  | ===========
[10 empty] | TOTAL: | 12450.5 | TOTAL: | 18657.5

## CIRCUIT 3
DELDOT | [11 empty] | Below, Input the distance to each load | [8 empty] | Below, Input the load from the luminaire or junction for each phase
| Job: |  | Project No. |  |  |  | Sheet: | 1 | of x
Description: |  | Voltage Drop |  |  |  | Calc. by: | XXX | Date: | 2019-03-25 12:51 |  |  |  | FROM | TO | DISTANCE (FT) | [8 empty] | NAME | PHASE A | PHASE B
Circuit: | [5 empty] | Checked by: |  | Date: |  |  |  |  | LCC | L136 | 85 | [7 empty] | Load 1: | L136 | 0.77
[13 empty] | L136 | L135 | 85 | [7 empty] | Load 2: | L135 |  | 2.26
VOLTAGE DROP CALCULATION | [12 empty] | L135 | L125 | 200 |  | Select the voltage of the system | [5 empty] | Load 3: | L125 | 2.26
[13 empty] | L125 | L126 | 190 | [7 empty] | Load 4: | L126 |  | 2.26
[13 empty] | L126 | JW | 60 | [7 empty] | Load 5: | JW | 6.78 | 4.52
|  | Voltage: | 120 | Total Amp-Ft of Worst Case: |  |  |  |  | 19449.65 |  |  |  | JW | L121 | 175 | [7 empty] | Load 6: | L121 |  | 2.26
[13 empty] | L121 | L122 | 125 |  | Voltage: |  | 120 |  |  |  | Load 7: | L122 | 2.26
| Voltage Drop (V): |  | 4.159 |  | Minimum Wire Size: |  |  |  | #2 |  |  |  | L122 | L123 | 180 | [7 empty] | Load 8: | L123 |  | 2.26
[13 empty] | L123 | L124 | 240 | [7 empty] | Load 9: | L124 | 2.26
| Voltage Drop (%): |  | 3.466% | [9 empty] | L124 | L129 | 230 | [7 empty] | Load 10: | L129 |  | 2.26
[13 empty] | L129 | L130 | 245 | [7 empty] | Load 11: | L130 | 2.26
| Percentage of Maximum Allowed Voltage Drop : | [7 empty] | 69.32% |  |  |  | L130 | L131 | 220 | [7 empty] | Load 12: | L131 |  | 2.26
Load 13:
Load 14:
Load 15:
TO USE CALCULATOR, INPUT DATA IN CELLS HIGHLIGHTED IN YELLOW. DATA UNDER SECTIONS HIGHLIGHTED IN PINK WILL AUTO-POPULATE. THEN SEE RESULTS IN THE RESULTS TO THE LEFT.
NOTE: ALL CALCULATIONS ARE MADE ASSUMING A MAX ALLOWABLE VOLTAGE DROP OF 5% AND USING ABOVE WIRE SIZE. ALL CALCULATIONS INCLUDE A 10% FACTOR TO ACCOUNT FOR DISCREPENCIES IN MEASUREMENTS OF THE CIRCUIT LENGTH
CONDUIT FILL CALCULATION
NOTE: CONDUIT FILLS ARE CALCULATED ASSUMING ONE CIRCUIT OF THE MINIMUM WIRE SIZE IN THE CONDUIT
| RGS: | % FILL |  | PVC Sched. 80: |  | % FILL | PVC Sched. 40: |  | % FILL
| 2" | 20.54% |  | 2" |  | 24.36% | 2" |  | 21.27%
| 2.5" | 14.39% |  | 2.5" |  | 16.99% | 2.5" |  | 14.91% | [7 empty] | See Calculations Below
| 3" | 9.335% |  | 3" |  | 10.87% | 3" |  | 9.631%
| 3.5" | 6.993% |  | 3.5" |  | 8.057% | 3.5" |  | 7.189%
| 4" | 5.434% |  | 4" |  | 6.218% | 4" |  | 5.576%
Max of 26% fill for new conduits
[14 empty] | Effect on total loads |  |  | Total Loads |  |  | Positive = ^ | Neg = v | [5 empty] | Area of Typical Wire Sizes |  |  |  |  | Area of Schedule 80 PVC Conduit (In2) |  |  |  | Area of Schedule 40 PVC Conduit (In2)
[10 empty] | From | To | Distance (ft) |  | Phase A | Phase B |  | A | N | B |  |  | IF Luminaire is on Phase A, Amperage is positive | [5 empty] | Circ. Mils | In2 |  |  |  | 100% | 26% | FILL |  | 100% | 26% | FILL
[10 empty] | LCC | L136 | 85 |  | 0.77 | 0 |  | 16.59 | 1.49 | -18.08 |  |  | If Luminaire is on Phase B, Amperage is negative |  |  |  |  | 4/0 | 211600 | 0.4754 |  |  | 2" | 2.874 | 0.74724 | 24.36% | 2" | 3.291 | 0.85566 | 21.27%
[10 empty] | L136 | L135 | 85 |  | 0 | -2.26 |  | 15.82 | 2.26 | -18.08 |  |  | If no luminaire appears on a phase, Amperage is 0 |  |  |  |  | 3/0 | 167800 | 0.4072 |  |  | 2.5" | 4.119 | 1.0709 | 16.99% | 2.5" | 4.695 | 1.2207 | 14.91%
[10 empty] | L135 | L125 | 200 |  | 2.26 | 0 |  | 15.82 | 0 | -15.82 | [7 empty] | 2/0 | 133100 | 0.6505 |  |  | 3" | 6.442 | 1.6749 | 10.87% | 3" | 7.268 | 1.8897 | 9.631%
[10 empty] | L125 | L126 | 190 |  | 0 | -2.26 |  | 13.56 | 2.26 | -15.82 | [7 empty] | 1/0 | 105600 | 0.3039 |  |  | 3.5" | 8.688 | 2.2589 | 8.057% | 3.5" | 9.737 | 2.5316 | 7.189%
[10 empty] | L126 | JW | 60 |  | 6.78 | -4.52 |  | 13.56 | 0 | -13.56 | [7 empty] | #1 | 83690 | 0.266 |  |  | 4" | 11.258 | 2.9271 | 6.218% | 4" | 12.554 | 3.264 | 5.576%
[10 empty] | JW | L121 | 175 |  | 0 | -2.26 |  | 6.78 | 2.26 | -9.04 | [7 empty] | #2 | 66360 | 0.175
[10 empty] | L121 | L122 | 125 |  | 2.26 | 0 |  | 6.78 | 0 | -6.78 | [7 empty] | #4 | 41740 | 0.1333 |  |  | Area of RGS Conduit (In2)
[10 empty] | L122 | L123 | 180 |  | 0 | -2.26 |  | 4.52 | 2.26 | -6.78 | [7 empty] | #6 | 26240 | 0.1041 |  |  |  | 100% | 26% | FILL
[10 empty] | L123 | L124 | 240 |  | 2.26 | 0 |  | 4.52 | 0 | -4.52 | [7 empty] | #8 | 16510 | 0.0835 |  |  | 2" | 3.408 | 0.88608 | 20.54%
[10 empty] | L124 | L129 | 230 |  | 0 | -2.26 |  | 2.26 | 2.26 | -4.52 | [12 empty] | 2.5" | 4.866 | 1.2652 | 14.39%
[10 empty] | L129 | L130 | 245 |  | 2.26 | 0 |  | 2.26 | 0 | -2.26 | [12 empty] | 3" | 7.499 | 1.9497 | 9.335%
[10 empty] | L130 | L131 | 220 |  | 0 | -2.26 |  | 0 | 2.26 | -2.26 | [12 empty] | 3.5" | 10.01 | 2.6026 | 6.993%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | [12 empty] | 4" | 12.882 | 3.3493 | 5.434%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[11 empty] | Ampere Ft Calc |  |  |  |  | Wire Size Calculations |  |  |  | Voltage Drop Calculations
[11 empty] | A-N |  | B-N |  |  | Total Ampere Ft. |  | 19449.65 |  | Area of wire required(cm): |  |  | 45998.4223 |  | Max allowed voltage drop (V): |  |  | 6
[11 empty] | 1283.5 |  | 1663.45
[11 empty] | 1152.6 |  | 1728.9 |  |  | Resistivity Constant: |  | 12.9 |  | Minimum necessary wire size: |  |  | #2 |  | Voltage drop using min wire size (V): |  |  | 4.159 |  | Voltage Drop in %: | 3.466%
[11 empty] | 3164 |  | 3164
[11 empty] | 2147 |  | 3435.2 |  | Maximum allowed voltage drop: |  |  | 5% |  |  |  |  | % of Max allowed Voltage drop using min wire size: |  |  |  |  | 69.32%
[11 empty] | 813.6 |  | 813.6
[11 empty] | 791 |  | 1977.5 |  |  | Voltage (V): |  | 120
[11 empty] | 847.5 |  | 847.5
[11 empty] | 406.8 |  | 1627.2 |  |  | Error Contingency: |  | 10%
[11 empty] | 1084.8 |  | 1084.8
[11 empty] | 0 |  | 1559.4
[11 empty] | 553.7 |  | 553.7
[11 empty] | 0 |  | 994.4
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | ========= |  | ===========
[10 empty] | TOTAL: | 12244.5 | TOTAL: | 19449.65

## CIRCUIT 4
DELDOT | [11 empty] | Below, Input the distance to each load | [8 empty] | Below, Input the load from the luminaire or junction for each phase
| Job: |  | Project No. |  |  |  | Sheet: | 1 | of x
Description: |  | Voltage Drop |  |  |  | Calc. by: | XXX | Date: | 2019-03-25 12:51 |  |  |  | FROM | TO | DISTANCE (FT) | [8 empty] | NAME | PHASE A | PHASE B
Circuit: | [5 empty] | Checked by: |  | Date: |  |  |  |  | LCC | L138 | 15 | [7 empty] | Load 1: | L138 | 0.77
[13 empty] | L138 | L140 | 130 | [7 empty] | Load 2: | L140 |  | 0.77
VOLTAGE DROP CALCULATION | [12 empty] | L140 | L141 | 70 |  | Select the voltage of the system | [5 empty] | Load 3: | L141 | 0.77
[13 empty] | L141 | L143 | 50 | [7 empty] | Load 4: | L143 |  | 0.77
[13 empty] | L143 | L142 | 135 | [7 empty] | Load 5: | L142 | 0.77
|  | Voltage: | 120 | Total Amp-Ft of Worst Case: |  |  |  |  | 12169.4 |  |  |  | L142 | JW | 80 | [7 empty] | Load 6: | JW | 2.26 | 2.26
[13 empty] | JW | JW2 | 100 |  | Voltage: |  | 120 |  |  |  | Load 7: | JW2 | 1.5 | 1.5
| Voltage Drop (V): |  | 4.1371 |  | Minimum Wire Size: |  |  |  | #4 |  |  |  | JW2 | L110 | 70 | [7 empty] | Load 8: | L110 |  | 2.26
[13 empty] | L110 | L109 | 215 | [7 empty] | Load 9: | L109 | 2.26
| Voltage Drop (%): |  | 3.448% | [9 empty] | L109 | L105 | 230 | [7 empty] | Load 10: | L105 |  | 2.26
[13 empty] | L105 | L104 | 235 | [7 empty] | Load 11: | L104 | 2.26
| Percentage of Maximum Allowed Voltage Drop : | [7 empty] | 68.95% |  |  |  | L104 | L103 | 250 | [7 empty] | Load 12: | L103 |  | 2.26
Load 13:
Load 14:
Load 15:
TO USE CALCULATOR, INPUT DATA IN CELLS HIGHLIGHTED IN YELLOW. DATA UNDER SECTIONS HIGHLIGHTED IN PINK WILL AUTO-POPULATE. THEN SEE RESULTS IN THE RESULTS TO THE LEFT.
NOTE: ALL CALCULATIONS ARE MADE ASSUMING A MAX ALLOWABLE VOLTAGE DROP OF 5% AND USING ABOVE WIRE SIZE. ALL CALCULATIONS INCLUDE A 10% FACTOR TO ACCOUNT FOR DISCREPENCIES IN MEASUREMENTS OF THE CIRCUIT LENGTH
CONDUIT FILL CALCULATION
NOTE: CONDUIT FILLS ARE CALCULATED ASSUMING ONE CIRCUIT OF THE MINIMUM WIRE SIZE IN THE CONDUIT
| RGS: | % FILL |  | PVC Sched. 80: |  | % FILL | PVC Sched. 40: |  | % FILL
| 2" | 15.65% |  | 2" |  | 18.55% | 2" |  | 16.2%
| 2.5" | 10.96% |  | 2.5" |  | 12.94% | 2.5" |  | 11.36% | [7 empty] | See Calculations Below
| 3" | 7.11% |  | 3" |  | 8.277% | 3" |  | 7.336%
| 3.5" | 5.327% |  | 3.5" |  | 6.137% | 3.5" |  | 5.476%
| 4" | 4.139% |  | 4" |  | 4.736% | 4" |  | 4.247%
Max of 26% fill for new conduits
[14 empty] | Effect on total loads |  |  | Total Loads |  |  | Positive = ^ | Neg = v | [5 empty] | Area of Typical Wire Sizes |  |  |  |  | Area of Schedule 80 PVC Conduit (In2) |  |  |  | Area of Schedule 40 PVC Conduit (In2)
[10 empty] | From | To | Distance (ft) |  | Phase A | Phase B |  | A | N | B |  |  | IF Luminaire is on Phase A, Amperage is positive | [5 empty] | Circ. Mils | In2 |  |  |  | 100% | 26% | FILL |  | 100% | 26% | FILL
[10 empty] | LCC | L138 | 15 |  | 0.77 | 0 |  | 10.59 | 1.49 | -12.08 |  |  | If Luminaire is on Phase B, Amperage is negative |  |  |  |  | 4/0 | 211600 | 0.4754 |  |  | 2" | 2.874 | 0.74724 | 18.55% | 2" | 3.291 | 0.85566 | 16.2%
[10 empty] | L138 | L140 | 130 |  | 0 | -0.77 |  | 9.82 | 2.26 | -12.08 |  |  | If no luminaire appears on a phase, Amperage is 0 |  |  |  |  | 3/0 | 167800 | 0.4072 |  |  | 2.5" | 4.119 | 1.0709 | 12.94% | 2.5" | 4.695 | 1.2207 | 11.36%
[10 empty] | L140 | L141 | 70 |  | 0.77 | 0 |  | 9.82 | 1.49 | -11.31 | [7 empty] | 2/0 | 133100 | 0.6505 |  |  | 3" | 6.442 | 1.6749 | 8.277% | 3" | 7.268 | 1.8897 | 7.336%
[10 empty] | L141 | L143 | 50 |  | 0 | -0.77 |  | 9.05 | 2.26 | -11.31 | [7 empty] | 1/0 | 105600 | 0.3039 |  |  | 3.5" | 8.688 | 2.2589 | 6.137% | 3.5" | 9.737 | 2.5316 | 5.476%
[10 empty] | L143 | L142 | 135 |  | 0.77 | 0 |  | 9.05 | 1.49 | -10.54 | [7 empty] | #1 | 83690 | 0.266 |  |  | 4" | 11.258 | 2.9271 | 4.736% | 4" | 12.554 | 3.264 | 4.247%
[10 empty] | L142 | JW | 80 |  | 2.26 | -2.26 |  | 8.28 | 2.26 | -10.54 | [7 empty] | #2 | 66360 | 0.175
[10 empty] | JW | JW2 | 100 |  | 1.5 | -1.5 |  | 6.02 | 2.26 | -8.28 | [7 empty] | #4 | 41740 | 0.1333 |  |  | Area of RGS Conduit (In2)
[10 empty] | JW2 | L110 | 70 |  | 0 | -2.26 |  | 4.52 | 2.26 | -6.78 | [7 empty] | #6 | 26240 | 0.1041 |  |  |  | 100% | 26% | FILL
[10 empty] | L110 | L109 | 215 |  | 2.26 | 0 |  | 4.52 | 0 | -4.52 | [7 empty] | #8 | 16510 | 0.0835 |  |  | 2" | 3.408 | 0.88608 | 15.65%
[10 empty] | L109 | L105 | 230 |  | 0 | -2.26 |  | 2.26 | 2.26 | -4.52 | [12 empty] | 2.5" | 4.866 | 1.2652 | 10.96%
[10 empty] | L105 | L104 | 235 |  | 2.26 | 0 |  | 2.26 | 0 | -2.26 | [12 empty] | 3" | 7.499 | 1.9497 | 7.11%
[10 empty] | L104 | L103 | 250 |  | 0 | -2.26 |  | 0 | 2.26 | -2.26 | [12 empty] | 3.5" | 10.01 | 2.6026 | 5.327%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | [12 empty] | 4" | 12.882 | 3.3493 | 4.139%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[11 empty] | Ampere Ft Calc |  |  |  |  | Wire Size Calculations |  |  |  | Voltage Drop Calculations
[11 empty] | A-N |  | B-N |  |  | Total Ampere Ft. |  | 12169.4 |  | Area of wire required(cm): |  |  | 28780.631 |  | Max allowed voltage drop (V): |  |  | 6
[11 empty] | 136.5 |  | 203.55
[11 empty] | 982.8 |  | 1864.2 |  |  | Resistivity Constant: |  | 12.9 |  | Minimum necessary wire size: |  |  | #4 |  | Voltage drop using min wire size (V): |  |  | 4.1371 |  | Voltage Drop in %: | 3.448%
[11 empty] | 583.1 |  | 896
[11 empty] | 339.5 |  | 678.5 |  | Maximum allowed voltage drop: |  |  | 5% |  |  |  |  | % of Max allowed Voltage drop using min wire size: |  |  |  |  | 68.95%
[11 empty] | 1020.6 |  | 1624.05
[11 empty] | 481.6 |  | 1024 |  |  | Voltage (V): |  | 120
[11 empty] | 376 |  | 1054
[11 empty] | 158.2 |  | 632.8 |  |  | Error Contingency: |  | 10%
[11 empty] | 971.8 |  | 971.8
[11 empty] | 0 |  | 1559.4
[11 empty] | 531.1 |  | 531.1
[11 empty] | 0 |  | 1130
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | ========= |  | ===========
[10 empty] | TOTAL: | 5581.2 | TOTAL: | 12169.4

## CIRCUIT 5
DELDOT | [11 empty] | Below, Input the distance to each load | [8 empty] | Below, Input the load from the luminaire or junction for each phase
| Job: |  | Project No. |  |  |  | Sheet: | 1 | of x
Description: |  | Voltage Drop |  |  |  | Calc. by: | XXX | Date: | 2019-03-25 12:51 |  |  |  | FROM | TO | DISTANCE (FT) | [8 empty] | NAME | PHASE A | PHASE B
Circuit: | [5 empty] | Checked by: |  | Date: |  |  |  |  | LCC | L1 | 65 | [7 empty] | Load 1: | L1 | 1.7
[13 empty] | L1 | JW11 | 60 | [7 empty] | Load 2: | JW11 | 3.4 | 1.7
VOLTAGE DROP CALCULATION | [12 empty] | JW11 | L10 | 35 |  | Select the voltage of the system | [5 empty] | Load 3: | L10 |  | 1.7
[13 empty] | L10 | L9 | 95 | [7 empty] | Load 4: | L9 | 1.7
[13 empty] | L9 | L8 | 40 | [7 empty] | Load 5: | L8 |  | 1.7
|  | Voltage: | 120 | Total Amp-Ft of Worst Case: |  |  |  |  | 3765.5 |  |  |  | L8 | L7 | 125 | [7 empty] | Load 6: | L7 | 1.7
[13 empty] | L7 | L6 | 105 |  | Voltage: |  | 120 |  |  |  | Load 7: | L6 |  | 1.7
| Voltage Drop (V): |  | 3.2364 |  | Minimum Wire Size: |  |  |  | #8 |  |  |  | L6 | L5 | 145 | [7 empty] | Load 8: | L5 | 1.7
Load 9:
| Voltage Drop (%): |  | 2.697% | [19 empty] | Load 10:
Load 11:
| Percentage of Maximum Allowed Voltage Drop : | [7 empty] | 53.94% | [13 empty] | Load 12:
Load 13:
Load 14:
Load 15:
TO USE CALCULATOR, INPUT DATA IN CELLS HIGHLIGHTED IN YELLOW. DATA UNDER SECTIONS HIGHLIGHTED IN PINK WILL AUTO-POPULATE. THEN SEE RESULTS IN THE RESULTS TO THE LEFT.
NOTE: ALL CALCULATIONS ARE MADE ASSUMING A MAX ALLOWABLE VOLTAGE DROP OF 5% AND USING ABOVE WIRE SIZE. ALL CALCULATIONS INCLUDE A 10% FACTOR TO ACCOUNT FOR DISCREPENCIES IN MEASUREMENTS OF THE CIRCUIT LENGTH
CONDUIT FILL CALCULATION
NOTE: CONDUIT FILLS ARE CALCULATED ASSUMING ONE CIRCUIT OF THE MINIMUM WIRE SIZE IN THE CONDUIT
| RGS: | % FILL |  | PVC Sched. 80: |  | % FILL | PVC Sched. 40: |  | % FILL
| 2" | 9.8% |  | 2" |  | 11.62% | 2" |  | 10.15%
| 2.5" | 6.864% |  | 2.5" |  | 8.109% | 2.5" |  | 7.114% | [7 empty] | See Calculations Below
| 3" | 4.454% |  | 3" |  | 5.185% | 3" |  | 4.595%
| 3.5" | 3.337% |  | 3.5" |  | 3.844% | 3.5" |  | 3.43%
| 4" | 2.593% |  | 4" |  | 2.967% | 4" |  | 2.661%
Max of 26% fill for new conduits
[14 empty] | Effect on total loads |  |  | Total Loads |  |  | Positive = ^ | Neg = v | [5 empty] | Area of Typical Wire Sizes |  |  |  |  | Area of Schedule 80 PVC Conduit (In2) |  |  |  | Area of Schedule 40 PVC Conduit (In2)
[10 empty] | From | To | Distance (ft) |  | Phase A | Phase B |  | A | N | B |  |  | IF Luminaire is on Phase A, Amperage is positive | [5 empty] | Circ. Mils | In2 |  |  |  | 100% | 26% | FILL |  | 100% | 26% | FILL
[10 empty] | LCC | L1 | 65 |  | 1.7 | 0 |  | 10.2 | -3.4 | -6.8 |  |  | If Luminaire is on Phase B, Amperage is negative |  |  |  |  | 4/0 | 211600 | 0.4754 |  |  | 2" | 2.874 | 0.74724 | 11.62% | 2" | 3.291 | 0.85566 | 10.15%
[10 empty] | L1 | JW11 | 60 |  | 3.4 | -1.7 |  | 8.5 | -1.7 | -6.8 |  |  | If no luminaire appears on a phase, Amperage is 0 |  |  |  |  | 3/0 | 167800 | 0.4072 |  |  | 2.5" | 4.119 | 1.0709 | 8.109% | 2.5" | 4.695 | 1.2207 | 7.114%
[10 empty] | JW11 | L10 | 35 |  | 0 | -1.7 |  | 5.1 | 0 | -5.1 | [7 empty] | 2/0 | 133100 | 0.6505 |  |  | 3" | 6.442 | 1.6749 | 5.185% | 3" | 7.268 | 1.8897 | 4.595%
[10 empty] | L10 | L9 | 95 |  | 1.7 | 0 |  | 5.1 | -1.7 | -3.4 | [7 empty] | 1/0 | 105600 | 0.3039 |  |  | 3.5" | 8.688 | 2.2589 | 3.844% | 3.5" | 9.737 | 2.5316 | 3.43%
[10 empty] | L9 | L8 | 40 |  | 0 | -1.7 |  | 3.4 | 0 | -3.4 | [7 empty] | #1 | 83690 | 0.266 |  |  | 4" | 11.258 | 2.9271 | 2.967% | 4" | 12.554 | 3.264 | 2.661%
[10 empty] | L8 | L7 | 125 |  | 1.7 | 0 |  | 3.4 | -1.7 | -1.7 | [7 empty] | #2 | 66360 | 0.175
[10 empty] | L7 | L6 | 105 |  | 0 | -1.7 |  | 1.7 | 0 | -1.7 | [7 empty] | #4 | 41740 | 0.1333 |  |  | Area of RGS Conduit (In2)
[10 empty] | L6 | L5 | 145 |  | 1.7 | 0 |  | 1.7 | -1.7 | 0 | [7 empty] | #6 | 26240 | 0.1041 |  |  |  | 100% | 26% | FILL
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | #8 | 16510 | 0.0835 |  |  | 2" | 3.408 | 0.88608 | 9.8%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | [12 empty] | 2.5" | 4.866 | 1.2652 | 6.864%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | [12 empty] | 3" | 7.499 | 1.9497 | 4.454%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | [12 empty] | 3.5" | 10.01 | 2.6026 | 3.337%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | [12 empty] | 4" | 12.882 | 3.3493 | 2.593%
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[11 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[11 empty] | Ampere Ft Calc |  |  |  |  | Wire Size Calculations |  |  |  | Voltage Drop Calculations
[11 empty] | A-N |  | B-N |  |  | Total Ampere Ft. |  | 3765.5 |  | Area of wire required(cm): |  |  | 8905.4075 |  | Max allowed voltage drop (V): |  |  | 6
[11 empty] | 884 |  | 221
[11 empty] | 612 |  | 306 |  |  | Resistivity Constant: |  | 12.9 |  | Minimum necessary wire size: |  |  | #8 |  | Voltage drop using min wire size (V): |  |  | 3.2364 |  | Voltage Drop in %: | 2.697%
[11 empty] | 178.5 |  | 178.5
[11 empty] | 646 |  | 161.5 |  | Maximum allowed voltage drop: |  |  | 5% |  |  |  |  | % of Max allowed Voltage drop using min wire size: |  |  |  |  | 53.94%
[11 empty] | 136 |  | 136
[11 empty] | 637.5 |  | 0 |  |  | Voltage (V): |  | 120
[11 empty] | 178.5 |  | 178.5
[11 empty] | 493 |  | 0 |  |  | Error Contingency: |  | 10%
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | 0 |  | 0
[11 empty] | ========= |  | ===========
[10 empty] | TOTAL: | 3765.5 | TOTAL: | 1181.5

## UTILITY-CABINET
DELDOT
| Job: |  | Project No. |  |  |  | Sheet: | 1 | of x | Select the Voltage of the system, and Amps of the cabinet |  |  |  |  | Below, Input the distance from the Utility feed to the Lighting Control Cabinet
Description: |  | Voltage Drop |  |  |  | Calc. by: | XXX | Date: | 2019-03-25 12:51
Circuit: |  | Utility XFMR to LCC |  |  |  | Checked by: |  | Date:
[10 empty] | Voltage: | 120 |  |  |  |  | FROM | TO | DISTANCE (FT)
VOLTAGE DROP CALCULATION | [15 empty] | XFMR | LCC | 225
|  | Voltage: | 120 | Total Amp-Ft of Worst Case: |  |  |  |  | 14373 | Cabinet Amps: | 100
| Voltage Drop (V): |  | 1.5323 |  | Minimum Wire Size: |  |  |  | 2/0
| Voltage Drop (%): |  | 1.277% | [6 empty] | TO USE CALCULATOR, INPUT DATA IN CELLS HIGHLIGHTED IN YELLOW. THEN SEE RESULTS IN THE RESULTS TO THE LEFT.
| Percentage of Maximum Allowed Voltage Drop : | [7 empty] | 83.23%
NOTE: ALL CALCULATIONS ARE MADE ASSUMING A MAX ALLOWABLE VOLTAGE DROP OF 5% AND USING ABOVE WIRE SIZE. ALL CALCULATIONS INCLUDE A 10% FACTOR TO ACCOUNT FOR DISCREPENCIES IN MEASUREMENTS OF THE CIRCUIT LENGTH
CONDUIT FILL CALCULATION
NOTE: CONDUIT FILLS ARE CALCULATED ASSUMING ONE CIRCUIT OF THE MINIMUM WIRE SIZE IN THE CONDUIT
| RGS: | % FILL |  | PVC Sched. 80: |  | % FILL | PVC Sched. 40: |  | % FILL
| 2" | 76.35% |  | 2" |  | 90.54% | 2" |  | 79.06%
| 2.5" | 53.47% |  | 2.5" |  | 63.17% | 2.5" |  | 55.42% |  |  |  |  | See Calculations Below
| 3" | 34.7% |  | 3" |  | 40.39% | 3" |  | 35.8%
| 3.5" | 25.99% |  | 3.5" |  | 29.95% | 3.5" |  | 26.72%
| 4" | 20.2% |  | 4" |  | 23.11% | 4" |  | 20.73%
Max of 26% fill for new conduits
[14 empty] | LOAD | [6 empty] | Area of Typical Wire Sizes |  |  |  |  | Area of Schedule 80 PVC Conduit (In2) |  |  |  | Area of Schedule 40 PVC Conduit (In2)
[14 empty] | A | N | B | [5 empty] | Circ. Mils | In2 |  |  |  | 100% | 26% | FILL |  | 100% | 26% | FILL
[14 empty] | 63.88 | 1.42 | -62.46 |  |  |  |  | 4/0 | 211600 | 0.4754 |  |  | 2" | 2.874 | 0.74724 | 90.54% | 2" | 3.291 | 0.85566 | 79.06%
[21 empty] | 3/0 | 167800 | 0.4072 |  |  | 2.5" | 4.119 | 1.0709 | 63.17% | 2.5" | 4.695 | 1.2207 | 55.42%
[21 empty] | 2/0 | 133100 | 0.6505 |  |  | 3" | 6.442 | 1.6749 | 40.39% | 3" | 7.268 | 1.8897 | 35.8%
[14 empty] | AMP-FEET | [6 empty] | 1/0 | 105600 | 0.3039 |  |  | 3.5" | 8.688 | 2.2589 | 29.95% | 3.5" | 9.737 | 2.5316 | 26.72%
[14 empty] | A | B | [5 empty] | #1 | 83690 | 0.266 |  |  | 4" | 11.258 | 2.9271 | 23.11% | 4" | 12.554 | 3.264 | 20.73%
[14 empty] | 14053.5 | 14373 | [5 empty] | #2 | 66360 | 0.175
[21 empty] | #4 | 41740 | 0.1333 |  |  | Area of RGS Conduit (In2)
[21 empty] | #6 | 26240 | 0.1041 |  |  |  | 100% | 26% | FILL
[21 empty] | #8 | 16510 | 0.0835 |  |  | 2" | 3.408 | 0.88608 | 76.35%
[26 empty] | 2.5" | 4.866 | 1.2652 | 53.47%
[26 empty] | 3" | 7.499 | 1.9497 | 34.7%
[26 empty] | 3.5" | 10.01 | 2.6026 | 25.99%
[26 empty] | 4" | 12.882 | 3.3493 | 20.2%
[13 empty] | Wire Size Calculations |  |  |  | Voltage Drop Calculations
[13 empty] | Total Ampere Ft. |  | 14373 |  | Area of wire required(cm): |  | 110783.1019 | Max allowed voltage drop (V): |  | 1.841
[13 empty] | Resistivity Constant: |  | 12.9 |  | Minimum necessary wire size: |  | 2/0 | Voltage drop using min wire size (V): |  | 1.5323 |  | Voltage Drop in %: | 1.277%
[12 empty] | Maximum allowed voltage drop: |  |  | 1.534% |  |  |  | % of Max allowed Voltage drop using min wire size: |  |  | 83.23%
[13 empty] | Voltage (V): |  | 120 |  | Minimum DelDOT allowed wire size: |  | #2
[13 empty] | Error Contingency: |  | 10%